# VOLUME 3

# TECHNICAL SPECIFICATIONS

Table of Contents

VOLUME 3	1

TECHNICAL SPECIFICATIONS	1

PROJECT OBJECTIVE	3

GENERAL REQUIREMENTS	3

Tender's Responsibilities	3

Human Resources	4

Logistical Resources	5

Technical Specifications	6

Complete Nature of the All-Inclusive and Fixed Price	6

Execution And As-Build Drawings	6

Requirements For Concrete Work – Concrete	6

GENERAL PROVISIONS FOR THE EXECUTION OF WORKS	8

Security And Access to the Construction Site	8

Construction Site Signs and Visibility Elements	8

Temporary Connections	9

Earthworks	9

Waterproofing	14

Walls - Plaster and Coating	14

Walls - Painting - Washing	15

Tile Flooring	17

Glazing / Aluminium Glazing	18

Aluminium Glazed Doors	18

Aluminium Glazed Windows	18

Mosquito Repellent	18

REQUIREMENTS FOR ELECTRICAL WORK	18

Lighting Points and Switches	19

Lighting Fittings	19

Power Points	20

Power Distribution	20

Supply And Installation of Electrical Appliances	21

Grounding of Installations	22

Air Conditioning	22

Solar photovoltaic (PV) system	23

Fire Safety - Detection and Protection	23

PLUMBING WORK	24

Supply And Installation of Sanitary Fixtures	25

SPECIFIC PROVISIONS	26

Installation of the Water Meter	26

Installation of an Electricity Meter	26

Security	27

Main Building	27

Additional requirements (where applicable)	28

APPENDICES	29

Technical Data Sheets Requested	29

# PROJECT OBJECTIVE

The purpose of this contract is to undertake general works for the benefit of the Puntland Maritime Police Force (PMPF). Specifically, the project involves the construction of a police station in Bossaso, Puntland State of Somalia

The order in which the work is carried out will be at the discretion of EUCAP Somalia.

# GENERAL REQUIREMENTS

## Tender's Responsibilities

The Contractor shall protect the interests of EUCAP SOMALIA and perform the work and have them performed in accordance with the documents referred to in the contract and shall draw up any other supplementary or detailed plans which may be necessary for the performance of the contract.

The requirements specified in this document are considered a minimum. Any submitted base offer that deviates from the specifications will only be considered to the extent that the technical proposal is able to provide a higher level of quality than the minimum requirements of the specifications.

This contract shall include the following activities, based on lump-sums:

- Prior to the start of construction activities, the contractor is required to carry out a detailed topographical survey of the proposed project site, measuring 210 m × 120 m, and share the finalized topographical map with the Project Manager.

- The Contractor is required to carry out a detailed geotechnical study and submit a complete geotechnical report to EUCAP Somalia, enabling informed assessment of soil bearing capacity and the determination of a safe and suitable foundation depth.

The Contractor shall have:

    - Visited and inspected the site and location of the works

    - Taken full and entire note of the plans and descriptions

    - Verified the plans and the preliminary bills of quantities

    - Asked for all and any necessary or relevant information, pertaining to and for the calculation of its all-included price.

    - Assumed full responsibility for the quality of the work. Any hidden defects or flaws in the quality of the work are the responsibility of the contractor, who is obligated to remedy all problems at their own expense.

    - Taken the responsibilities for all costs related to site preparation, transportation of materials and labour, and their installation on site.

Furthermore, the Contractor shall:

- Ensure a high-quality level of work in accordance with the national standards for civil and mechanical work. The Contractor will have the work executed only by an experienced labour force.

- Bear full responsibility for implementing all safety procedures including PPE in compliance with all applicable safety and labour laws and bear full responsibility for any accidents arising from the normal execution of the work.

- The materials used and the execution of the works must comply with the technical requirements from appendix and, in general, with applicable international construction standards.

- Ensure that local services are disrupted for the minimum duration of time during work, and coordinate with the relevant authorities, to warn any potentially affected people of any necessary shutdowns.

- Clean the site and take good care of it during work. All debris, garbage, waste materials and construction equipment used during the project must be taken out of the work site for termination or completion of the contract.

- Keep, of its own volition, the Contracting authority informed of unforeseen or significant occurrences or difficulties, particularly in the event of a delay in the work and supply the Contracting authority with the information the latter requests.

## Human Resources

The tenderer will be responsible for employing, for the entire duration of the works, at a minimum:

| Functions | Minimum qualifications required | Minimum numbers required |
| --- | --- | --- |
| Site Supervisor | Civil Engineering, master’s degree or Bachor degree with 10 years of experience in construction projects and at least 2 experiences as a site manager for similar projects | 1 |
| Electrical Works Supervisor | Electrical or Energy Engineering degree (or equivalent, master’s level) with 10 years of experience in the field and at least two years of experience as an electrical team leader on similar projects or include in your application a collaboration agreement with an accredited electrical engineering firm. | 1 |
| Site Supervisor | Holder of a technical diploma in Civil Engineering/Building Design with 7 years of experience in building construction work | 1 |
| Certified electrician | Holder of a vocational diploma in electricity/electromechanics with 5 years of experience in the field or a vocational certificate in electricity with 8 years of experience | 1 |
| Qualified plumber | Holder of a Vocational Certificate in Plumbing with 3 years of experience or a Technician's Certificate in Hydraulics with 5 years of experience in the work or a professional training certificate in plumbing with 7 years of experience. | 1 |

If the tenderer cannot meet these requirements, the contracting authority will reject its offer.

In the event of the replacement of this staff by the successful tenderer, the latter will undertake to assign to the execution of the contract staff with at least equivalent qualifications and skills, so that this replacement does not affect the schedule and quality of services.

## Logistical Resources

The tenderer will be responsible for having in their possession (purchased or rented) for the entire duration of the works at a minimum:

| Designations | Minimum numbers required | Status |
| --- | --- | --- |
| Liaison vehicle* | 1 | Bought |
| 10m³ dump truck* | 1 | Purchased or rented |
| 10 m3 water tanker truck* | 1 | Purchased or rented |
| TOPO LEVEL DEVICE | 1 | Purchased or rented |
| TOPO TOTAL STATION Device | 1 | Purchased or rented |
| 350-litre concrete mixer | 2 | Bought |
| Three vibrating needles | 2 | Bought |
| Metal props | 500 | Rent/Bought |
| Scaffolding | 120 | Rent/Bought |
| 16kg Handheld soil compactor | 1 | Bought |
| Set of small tools (shovel, hammers, trowels, float, clamps, etc.) | 1 | Bought |
| Safety equipment kit (shoes, boots, helmets, vests, gloves and goggles etc.) | 1 | Bought |

The tenderer must provide documents that attest to the ownership or rental of the resources.

*A valid registration certificate is mandatory for the following vehicles: tipper trucks; tanker trucks and liaison vehicles.

# Technical Specifications

The purpose of this document is to define all the work necessary for the construction of new police station building for PMPF.

It is important to note that the specifications below are not exhaustive and that companies must include in their offers all materials, equipment, and supplies necessary for the proper execution of the work, even if these are not expressly described herein. It will be their responsibility to identify any gaps or omissions.

Any violation or non-compliance found with the requirements set out in this document gives the beneficiary the right to stop the work until all discrepancies are rectified.

## Complete Nature of the All-Inclusive and Fixed Price

To avoid omissions and duplication, the contractor is required to review the technical specifications and plans of other trades that may inform them about the work they are required to plan and carry out.

## Execution And As-Build Drawings

The contractor will execute, at their own expense, the execution plans, which they will submit to the project manager for approval before any actual commencement of said work. They must make the approved plans available on the construction site and provide copies to the project managers and the delegated contracting authority.

Without the provision of plans approved by the contracting authority or project manager, the contractor cannot begin work. Starting work without approved plans entitles the project manager to demand the demolition of the work and its reconstruction at the contractor's expense.

At the end of the work, the contractor will execute all the plans and drawings used for the construction project; these plans will show all the modifications that occurred during the execution. The detailed plans of all underground networks are brought into conformity with the works as they were carried out.

All these plans and diagrams together constitute the as-built plan.

- The contractor is responsible for preparing all plans and documents related to the actual execution of the work. This includes reinforcement detailing schedules and supporting plans or documents relating to any elements that the contractor intends to implement differently from the original design.

- The final plans for the location of cable trays (electricity), plumbing and for all building-related activities.

## Requirements For Concrete Work – Concrete

Concrete work includes, but is not limited to, lean concrete, footings, stringers, floor slabs, and concrete in elevation (beams, isolated and continuous footings, stringers, lintels, tie beams, windowsills, columns, etc.). Included in the package are all supplies, their transport to the work site, and the preliminary tests, trials and surveys which are expressly the responsibility of the company.

The compressive and tensile strengths must be at least equal to those shown in the table below:

| Duration | 7 days | 28 days | 90 days |
| --- | --- | --- | --- |
| Compression | 170kg/cm² | 250kg/cm² | 270 kg/cm² |
| Traction | 17 kg/cm² | 25 kg/cm² | 27 kg/cm² |

The materials used for the concrete will be of consistent colour and quality to ensure a homogeneous concrete with a uniform shade. The contractor will also take all necessary measures to guarantee a consistent surface appearance, particularly when repairing gravel pockets that do not compromise the structure's stability.

The minimum required for the design of concrete structures must be 30 N/mm2 (Compression strength class C25 / 30).

The concrete mix design must be submitted for approval before the concrete works are implemented. The steel reinforcements must be of standard diameter and of Fe E500 quality and installed according to construction standards.

A minimum concrete thickness must be maintained to prevent corrosion of the reinforcement bars. The bars must be placed at a minimum distance of 50 mm from the ground if it is not previously covered with an insulating membrane or a layer of lean concrete. For exterior surfaces (columns, beams etc…) the irons must be at a minimum distance of 25 mm from the walls.

To comply with the minimum thicknesses seen above, concrete spacer blocks will need to be used to raise the metal reinforcements.

All forms of steel reinforcement must be fixed in accordance with the requirements of the compliance standards. The iron reinforcements must overlap and be held together by means of a steel wire. The overlap of the rebar between the vertical reinforcement from the foundations and that of the columns must be at least 500 mm for 8 mm diameter reinforcement, 600 mm for 10 mm diameter reinforcement, 700 mm for 12 mm diameter reinforcement and 950 mm for 16 mm diameter reinforcement.

All construction projects requiring the use of vibratory or air-blown methods to ensure homogeneous concrete distribution must be designed by professionals. These methods demand rigorous controls and tests to guarantee the highest final product quality.

The tenderer must protect the concrete so that it is maintained at a temperature between 10°C and 35°C for a period of 7 days. The contractor must maintain a certain level of moisture in the concrete to facilitate the hardening phase for a minimum of 7 days after placement. The contractor must monitor the process to ensure that not too much water is used, nor that the concrete dries out.

The concrete must comply with the construction standards. The reinforced concrete will have a mix of 350 kg/m³ and must meet at least the following requirements:

- The use of crushed aggregates (high angle of internal friction).

- The use of well-graduated, tumbled sand.

- A low water content (around 125 l/m3) hence the need for a plasticizer.

- High consistency (Abram’s cone slump of approximately 3 cm).

- The contractor must take at least 9 cu.m for each concrete pour, for compressive strength testing of the mix. All these cubes will be tested according to the standards applicable in Somalia or internationally, and the results will be submitted to the project manager for approval.

Immediately after pouring and for at least five (5) days afterwards, the concrete must be protected against the harmful effects of weather including rain, rapid temperature changes and against rapid drying, by appropriate approved protection and curing procedures.

At the request of the beneficiary, the supplier must present the quality certificates for the concrete and materials used.

# GENERAL PROVISIONS FOR THE EXECUTION OF WORKS

## Security And Access to the Construction Site

The tenderer must fence off and secure the construction site area day and night at their own expense and implement an action plan to prevent occupational injuries.

The worksite must be marked and signposted to alert personnel to its presence. Hazardous areas will be illuminated at the contractor's expense, as needed, and with sufficient lighting to prevent accidents.

All openings and passageways must be securely sealed at night. Security strips are insufficient and not acceptable.

The contractor will carry out, at their own expense, the site preparation and access work for the passage of construction vehicles. They may not claim any additional charges for these extra preparation costs.

The contractor must ensure the cleanliness and good order of his worksite, in accordance with local regulations and instructions from the relevant authorities.

Generally, except for project staff and personnel involved in the project and the company's workers, access to the construction sites will be strictly prohibited to anyone not directly involved in the work. The contractor will install, at its own expense, barriers, fences, and all necessary installations to ensure safe traffic flow and isolate the construction site from the public road.

Given that the beneficiary's personnel will be present within the site perimeter, the tenderer must take all necessary measures to strictly implement all security protocols. The tenderer must ensure that any information or documents (plans, photographs, recordings, etc.) concerning premises belonging to the PMPF are not disclosed by its personnel. The tenderer will be held responsible for any breach of site security resulting from non-compliance with this measure and will be held accountable for the consequences.

All phases of the project must be closely coordinated with the beneficiary's representative.

## Construction Site Signs and Visibility Elements

The successful tenderers will be responsible for installing a construction site sign containing descriptive information about the contract. All details will be provided and approved by the contracting authority.

## Temporary Connections

The contractor must carry out all necessary temporary works to supply the construction site at their own expense. They cannot use supply difficulties as a pretext for delays.

## Earthworks

This will involve preparing and levelling the land and setting out the structures. The tenderer will be responsible for levelling the land before any construction begins. The land must be made as flat as possible.

    - Excavation Work

- Excavations for isolated footings

The excavations for isolated footings will extend down to firm ground (the depth will depend on the geotechnical report) to a depth of between 1200 mm and 1500 mm. The dimensions of the excavations will be determined in the structural details. The depths and dimensions of the excavations under isolated footings and those of the trench excavations are given in the execution plans.

The excavation base will first be leveled, watered, and thoroughly compacted before a layer of lean concrete, 50 - 70 mm thick, with a minimum cement content of 150 kg/m³, is poured (a polyurethane membrane will also be laid where necessary). A layer of lean concrete must be placed under all structures in direct contact with the ground.

An anti-termite treatment will be carried out on the foundation excavations and the slabs (platforms), under all expansion joints in the slabs and at the connections between the slabs and the foundation beams. Before backfilling the excavations and at each 20 cm layer of backfill, an anti-termite product will be poured. Before any concrete work begins, the bottom of the excavations will be carefully tamped and compacted to prevent any subsequent settlement of the foundations, foundation beams, and slabs.

- Excavations in ditches or holes

All excavations, whether by pit or trench, regardless of the soil type, for the construction of foundation blocks, isolated footings, and pits, as indicated on the execution plans and to the project dimensions, will be required. The excavated soil will be temporarily stockpiled for later reuse (if its geotechnical characteristics permit), according to the Engineer's instructions.

- Debris

The contractor will be free to use the means of removal that he deems most advantageous to his/her interests, if this does not entail any additional burden for the Works and that the deadlines set for execution are fully respected.

The contractor must ensure the existence of any gutters, sewers, drains, pipes or other installations to avoid any damage that may be caused by the excavation work.

The contractor may use the excavated soil, provided that this soil meets the following quality definition:

- The fill material must be homogeneous, of good quality, free from clay, large or plant debris and other organic matter (pieces of wood, plastic waste and others).

- The contractor must submit the quality of fill he intends to use to the approval of the engineer in charge of directing the works.

- Compaction

Compaction will be carried out in layers of 0.2m average thickness, over a sufficient length.

No new layer may be laid until the previous layer has been properly compacted and levelled, in accordance with the standards set by the project management, taking into account preliminary laboratory tests carried out on samples of the fill or the base of the foundation, as well as the compaction results of a test area (compaction method and moisture content). Compaction must reach 95% of the OPM (Occupational Moisture Strength).

    - Formwork and Stripping Work

The price of the Formwork is included in the price of the concrete works. They will be sufficiently rigid to prevent any deformation and withstand the compaction or vibration of the parts and designed in such a way that they allow for demoulding without damage.

They must remain sufficiently watertight during the concrete pouring to prevent cement slurry leakage. The gap between the boards must never exceed 5 mm.

The reinforced concrete parts intended to remain visible will be poured into special forms, such as plywood, planed boards, etc., the joints of which will be carefully fitted to prevent the flow of laitance.

If the formwork results in burrs, bulges, sagging, hollows, bumps, etc., the company is required to carry out mandatory levelling or sanding.

Formwork shoring – The loads allowed on the shoring will be 1.5 to 3 times the load due to the concrete.

The supports under the beams will consist of crossbeams with two supports or a single support, spaced 60 to 80 cm apart for wooden supports and 1 to 1.50 m apart for metal supports made of 40/49 mm diameter tubes.

When the supports are made of logs, the average diameter will be 12 cm for a height of 3 to 5 m.

When squared timbers, or beams are used, they will be assembled using buttons, hooks or nails.

For heights greater than 5 m, the props may be made in 2 pieces in the following proportions: 50% under the floors; 35% under the beams, the joint being made in the upper 1/3 or in the lower 1/3 by assembly with three nailed planks of length at least equal to 70 cm for rounds and with two nailed planks for squares.

The supports for the props will consist of rafts of sufficient length, distributing the pressure exerted on them: they will be wedged with hardwood wedges. The supports will be held in place, depending on the case, by interlacing in one direction or in two orthogonal directions.

Formwork removal – This will be carried out without shock and by static forces when the concrete has acquired a hardening that allows it to withstand the stresses to which it will be subjected after formwork removal. Formwork removal times will depend on the type of cement, the outside temperature, and the stresses to be withheld. Formwork removal for cast-in-place structures will not take place before:

- 2 days for vertical faces.

- 21 days for horizontal faces.

For pieces cast on the floor, only maintaining the shape after formwork removal determines the drying time with formwork.

These parts may only be moved or transported 21 days after their manufacture, unless a special method is used to accelerate their setting and hardening. This method must be submitted to the EUCAP Project manager for approval.

Prefabricated parts must be lifted and transported in such a way that no stress, incompatible with the resistance of these elements, appears.

    - Implementation of Reinforcement

- Cleanliness: the frames must be clean, stored away from rain and any soiling (oil, paint, dirt, etc.).

- Erection and bending: the frames are carefully erected or bent using templates, according to the prescribed shapes and dimensions.

- The folding is done slowly and gradually so that any cracking or deterioration is avoided.

- Crossing: The intersecting reinforcements are tightly pressed against each other at each crossing point by steel wire ties while respecting the necessary overlaps.

- Placement and maintenance of reinforcement – ​​No reinforcement may remain exposed after formwork removal. If this occurs, the project manager reserves the right to refuse construction and have it demolished and rebuilt at the contractor's expense. The contractor will take all necessary precautions (spacers, shims, chairs, etc.) to ensure compliance with the prescribed standards regarding, firstly, the minimum distance between reinforcement and formwork, and secondly, the minimum distance between parallel bars.

- It is strictly forbidden to lift the reinforcement bars during and after concreting.

- The price of the reinforcement is included in the unit price of the concrete structures.

Note: All reinforcing bars will be of standardized diameters. Measurements will be taken on site, and those that do not meet specifications will be rejected and shipped off the site.

    - Infrastructure Works – Foundations

The foundations will be designed according to the loads to be transmitted and the allowable bearing capacity of the subgrade soil, based on the conclusions of the geotechnical studies, which will be submitted to the engineer for approval. The dimensions of the concrete slabs will be calculated at the serviceability limit state.

NB: All foundations will be made of CEM II concrete dosed at 350 kg/m³.

The twisted steels used will be of the High Adhesion type with a stress of 500 MPa and will conform to their approval sheet.

The formwork used will be of the basic type.

- Thick concrete foundation

The sizing of the large concrete structure will be done at the serviceability limit state, the most unfavourable case.

Pouring of heavy concrete at 250 kg/m³ with CEM II cement below the isolated reinforced concrete footings, masonry, a minimum depth of 100 cm will be provided depending on the nature of the soil.

The excavation base must be clean, free from collapsed earth or debris.

- Lean concrete

Pouring of a lean concrete at 150 kg/m³ with CEM II cement under all reinforced concrete foundations, masonry or other materials in contact with the ground, a minimum lean concrete layer of 0.05 m thickness will be provided.

The excavation base must be clean, free from collapsed earth or debris.

The price applies per cubic meter of concrete used in the execution of the work.

- Reinforced concrete 350 kg/m3, for isolated footings, foundation columns, and beams

At the point loads under the columns, isolated footings on heavy concrete will be provided. Their dimensions will depend on the design loads and the allowable stresses of the foundation soil.

Special structures such as staircases will rest on foundation blocks independent of the other foundations. Constructed in accordance with the architectural plans and using reinforced concrete.

Construction of all reinforced concrete stringers on foundation walls as shown in the execution plans, and of all the various works attached thereto.

These reinforced concrete structures implicitly include formwork constraints, drip edges, rebates and hoppers, pipe passages, cleats, sealing holes, etc., …

This position includes formwork, reinforcement, and all implementation constraints. The price applies per cubic meter of concrete used in the execution of the work.

Concerned: The foundations, support posts, stringers.

- Foundation walls

The contractor will be responsible for the following:

- Masonry foundations made of 400 cm solid concrete blocks. These foundations will be raised by reinforced concrete beams.

- Reinforced concrete

The contractor will be responsible for constructing the reinforced concrete slab on a solid base covered with polyethylene film across the entire interior surface of the buildings, in accordance with the specifications in the drawings. This slab will receive either a sealed coating or a waterproof cement screed.

    - Concrete Superstructures and Floors

- Reinforced concrete in elevation

This section considers all reinforced concrete frame structures from the ground floor slab to the roof.

The load-bearing structure in elevation will consist of columns, beams and reinforced concrete slabs.

These reinforced concrete structures implicitly include, in addition to formwork, reinforcement and concrete placement, all formwork constraints, drip edges, rebates and hoppers, pipe passages, cleats, sealing holes, etc.,

These concrete structures will be made of concrete dosed at 350 kg/m³ of CEM II cement.

The twisted steels used will be of the High Adhesion type and of stress 500 MPa and will conform to their approval sheet.

The formwork used will be of a neat type intended to remain visible.

- Various concrete

Construction of all steps, access ramps and bases in poured concrete dosed at 250 kg of CEM II cement / m3 as shown on the execution plans.

The visible exterior walls will be coated with cement mortar.

The sloping forms of the various terraces planned in this project will be constructed using lean concrete with a cement content of 300 kg per cubic meter, perfectly levelled. These sloping forms will be poured directly onto the terrace floor, the surface of which will have been left unfinished to improve adhesion.

The slopes must not be less than 0.01 m per meter along the diagonals. At the lowest point, the thickness must not be less than 300 mm.

Since the slope is poured directly onto the terrace floor, no joints will be required. Grooves must be installed at all upstands. The slope will be between 1 and 5%, and the roof surfaces will be flat.

This position includes formwork and all implementation constraints.

- Walls made of solid concrete blocks

In the basic solution and unless otherwise indicated in the quote, all exterior and interior masonry in elevation will be made of concrete blocks and that in foundation will be made of stone of 400cm thick.

The masonry of solid blocks of 20 cm x 20 cm x 40 cm, will be in homogeneous mortar of (1:3) mixture, unreinforced, of various aggregates and of artisanal or industrial manufacture.

They must be free of defects such as cracks, deformation, or tearing; their faces must be flat and their edges straight. The faces intended to be plastered must be rough and exhibit good adhesion to the plaster. The aggregates must be natural sand aggregates, free from any plant debris, soil, or clay lumps. "Dust" sand is excluded, and the mixture must contain the required percentage of heavy gravel.

The blocks must be of uniform dimensions, have straight corners and perfectly flat faces, and have received prior approval from the project manager. These blocks must be prepared at least 15 days before their installation.

The work will be carried out in such a way as to obtain a masonry with well-bonded elements. The masonry will be laid in courses with staggered joints, each block overlapping those of the course below by at least 10 cm. The shortest distance between a vertical joint and the edge of an internal or external corner will be at least 20 cm. The thickness of the beds and joints will be 1 to 1.5 cm.

The practice of re-beating mortar is prohibited. Any mortar that is dried out or beginning to set cannot be used.

Stairs

Construction of the reinforced concrete stairs as shown in the execution plans. The treads and risers will be delivered unfinished to receive a covering. Care must be taken in the execution of these works to respect the given altimetry.

The price applies to cubic meters of concrete used in the execution of the work.

## Waterproofing

The contractor will take the necessary precautions to prevent any water infiltration, including adjusting the slope, installing enough gutters, etc. Light weight roof screed comprising cement, sand and pumice (1:3:7), finished with a 10mm layer of cement and sand (1:4) topping, laid on concrete and finished to receive 3 layers roofing felt (Bitumen membrane).

The supplier must use the highest quality materials. To this end, the supplier must provide quality certificates and technical specifications before commencing work. The proposed solution must be presented to the contracting authority for approval. Otherwise, the contracting authority may refuse the work and request its reinstatement under the contract, at the tenderer's expense.

## Walls - Plaster and Coating

    - Wall Covering Tiles

The characteristics of the tiles must be guaranteed by technical data sheets justifying the tile quality and/or ensuring they match the existing tiles in colour and texture for a consistent look in the room. Due to market shortages, the contractor may present alternative types to the project manager. For wall coverings to be bonded to a cement mortar base, installation will be carried out using special adhesive mortars approved by the project manager. The minimum finished height will be 1.8 meters. Grouting will be done with pure white cement grout.

    - Mortar Plastering Work

Cement mortar plastering work includes:

- The preparation of the supports, execution of straightening works including all supplies, of the different constituent layers of the plasters, including all constraints of pickling, angles, joints.

- The supply of scaffolding and equipment necessary for the work, their installation and removal.

- The removal of all waste and rubble resulting from the works and their transport to a public landfill.

- A finishing coat provides the appearance of the finished plaster and completes the waterproofing. This finishing coat will be replaced with a textured and graded aggregates resin bonded plaster, as indicated on the BoQ.

Once the binder has started to set, the mortar cannot be folded back under any circumstances.

Plastering cannot be carried out when the substrates are overheated or dried out, or during dry winds (harmattan). With the project manager's authorization, certain measures may be taken to mitigate these problems, including protecting the substrates from overheating, moistening dried-out substrates throughout, and protecting the plaster from sun or dry winds by applying moistened screens. Plaster should not be moistened during the curing process in hot, dry weather; it should be done in the morning and evening. Structural joints will extend through the entire thickness of the plaster.

Quality of binders–The binders used will be neither stale nor “clumpy,” meaning they will not contain any lumps that cannot crumble under finger pressure. They will be stored protected from the elements and humidity.

Aggregate quality – Sands

- The sands will preferably be siliceous sands rather than mixed or calcareous sands.

- Under no circumstances will micaceous, marly, clayey or gypsum sands be used.

- They must not contain any fine elements below 1/3 mm and, as far as possible, elements above 3 mm.

- They will be dry, crunchy, leaving no residue in the hand and not clumping together after being squeezed.

Aggregate Quality – Gravel–They will have the same characteristics as sands, their grain size depending on their intended use.

#### Treatment of cracks

For minor cracks, swelling or peeling of the plaster, the contractor will proceed to scrape the affected surface and apply plaster.

For medium or deep cracks, the contractor will cut channels down to the origin of the crack, then install wire mesh, 6 mm diameter rebar, or any other suitable method approved by the engineer. This process will be followed by filling the crack with cement mortar or concrete, depending on the type of material affected, in 5 cm increments until it is filled. The joint will be made with the undamaged surface, ensuring a flat surface.

## Walls - Painting - Washing

    - Paint

The painting work will include, but is not limited to:

- The supply and implementation of all products and means of execution.

- Preparing the supports.

- The provision of colour samples and paint tests to be carried out at the request of the project manager.

- The application of interior and exterior smoothing plaster in 3 coats including correction and sanding.

- The fittings, rework and touch-ups after adjustment and testing.

- Precautions to take during the work to protect parts that are not to be painted, such as hardware, flooring, etc.

- Exterior and interior water-repellent painting work on a volume.

- Painting work on metalwork.

- The usual cleaning (floors, woodwork, etc.).

Before applying the new coat of paint, the painter will clean the surface by scraping or by any other suitable means.

Surface preparation work is carried out before any painting or plastering begins. This includes sanding, dusting, washing or degreasing, filling holes, removing rust from metal, and removing soot stains. Care must be taken to ensure that painting is carried out on perfectly dry surfaces.

Dusting will be carried out with a broom on the ceiling and from bottom to top on the walls before the application of plaster or any coat of paint.

Brushing and sanding will be carried out with the utmost care. A stiff or wire brush will be used to remove all traces of rust and mill scale from woodwork, and a dry or wet brush will be used on metal and masonry surfaces. No trace of mortar, plaster, etc., should remain.

The impregnation and primer coats will be applied with a brush, paintbrush, or roller and carefully smoothed for perfect adhesion. This layer of paint only provides temporary rust protection between installation and the final painting.

Filling involves blocking small holes or cavities that remain on the surface. It also includes perfectly executed plastering or sealing, concealing cracks, fissures, irregularities, crevices, and small cavities. This is done after the primer coat or over a partial priming. Cracks, holes, and fissures will first be opened with hooks on flared walls, then moistened and filled. After complete drying, a primer coat and a plaster will be applied.

The smoothing plasters will completely cover the masonry surfaces to be painted, with pores and cavities being perfectly filled.

Sanding allows for the correction of any imperfections that could negatively impact the surface finish after plastering, filling, or skimming. For very precise work, it is done with a sanding block or wet/dry sandpaper; otherwise, with dry sandpaper or dry abrasive paper.

The contractor must carry out all preparatory operations such as sanding, grinding, dusting, whether detailed or not in the descriptive estimate.

The paint layers will be sufficiently thick. Each coat will be properly overlapped and then smoothed. A new coat will only be applied after a complete inspection, with any imperfections and irregularities smoothed out and any drips or runs scraped off. No coat will be applied over another until the previous coat is completely dry. Test areas will be prepared beforehand and submitted to the project manager for approval. The colors will be consistent, with no perceptible difference from one part of the same room to another, and in all cases, conforming to the sample or the previously prepared test area. Touch-ups must be imperceptible, even for water-based silicate paints, where, in the latter case, applications made on clearly defined areas may be touched up. The colours will be specified by the project manager and will only be definitively adopted upon his agreement, formulated based on samples in place which will have a minimum surface area of ​​one square meter.

    - Water-Based Paint, Waterproof Type

All interior and exterior masonry surfaces of walls and buildings (except wet rooms), as per the plans and specifications, will be painted with a water-based, water-repellent satin-type acrylic paint (FOM type). It will be applied in three coats. The contractor must consult with the project manager regarding colour selection.

## Tile Flooring

# A). General characteristics:

The criteria used are:

- the regularity of the tile dimensions: length, width, thickness, angularity.

- the regularity of appearance and shade in the chosen color.

- the chemical characteristic that gives resistance to acids and alkalis.

- the physical characteristics giving homogeneity, water absorption coefficient and wear resistance.

- the mechanical characteristics giving resistance to breakage by bending and punching.

B) Method of applying and installing the coatings:

Porcelain stoneware tiles, in particular Italian porcelain tiles will be applied to the floors delivered unfinished by the structural work.

The tiles will be laid on a mortar bed of 3 cm of minimum thickness, with SIKALITE type additive in wet and sanitary rooms and grout between joints in ready-to-use joint mortar type LATICRETE or BUCHTAL or similar.

Tile joints:

The tiles will be laid with reduced joint widths.1 mm wide with ready-to-use joint mortar filling grout with Laticrete 3701 additive.

- Matte porcelain stoneware 60 x 60

Supply and installation of 60 x 60 cm polished porcelain stoneware tiles by 5mm Imported unglazed tiles, U4 P3 classification, color to be chosen by the architect. Tiles with rounded edges (1 and 2) are required for external corners.

- Porcelain stoneware 30 x 30

Supply and installation of 30 x 30 cm porcelain stoneware tiles by 5mm Imported unglazed tiles, U4 P3 classification, color to be chosen by the architect. Tiles with rounded edges (1 and 2) are required for external corners.

# Bathroom installation

- For Bathroom installation- Execution of GC 30 x 30 anti-slip floor coverings for bathroom floors.

- In baseboards

Implementation: Supply and installation of straight skirting boards in WINCKELMANS porcelain stoneware ditto art.

# Straight baseboards 600 x100mm with inside and outside corner or mitre cut in porcelain stoneware.

## Glazing / Aluminium Glazing

The glazing of standard frames will be made of single clear (or tinted) glazing as appropriate, with a minimum thickness of 5 mm.

The glass panes will be cut or prefabricated to ensure the required clearances specified in the DTU (Unified Technical Documents) or by the manufacturer. The panes will be installed under glazing beads in a special sealant bath that does not require protective painting. In all cases, the installation of the glazing will be carried out according to the DTU regulations.

## Aluminium Glazed Doors

They will be manufactured according to the dimensions indicated on the plans or specifications, with two glazed aluminum sashes. The glass will have a tinted, uni-vision type texture, meaning it is tinted from the inside out. The glass thickness will be a minimum of 5 mm, resistant to temperature variations and impacts. They will be supplied with a security lock, type "C" as described above, and retaining wedges securely anchored to the exterior walls in alignment with window retaining wedges, as well as top and bottom stops and hooks. Flat bars for reinforcing the slats will be attached to the interior side. They will slide using integrated rails or tracks.

## Aluminium Glazed Windows

They will be made according to the dimensions indicated on the plans or quotes and will all be made of aluminium.

## Mosquito Repellent

All window frames will be fitted with high-quality, fine-mesh screens (resistant to wind, won't break when bent, and ensures consistent openings that remain fixed in position). These screens will be installed before the windows are fitted and will be mounted on rotating or sliding supports.

# REQUIREMENTS FOR ELECTRICAL WORK

The tenderer will be responsible for carrying out the electrical installations in accordance with the international standard, which regulates electrical installations in low voltage. All electrical equipment must be CE marked and comply with applicable European standards. The cable color code below must be followed:

- Brown (red), black and grey for phases L1, L2 and L3.

- Blue for neutral.

- Green and yellow for the grounding cable.

If applicable, all cables must be protected by conduits or trunking. For buried cable runs, the cables will be placed in flexible conduits. The conduits will be accessible via pull boxes spaced a maximum of 25 m apart. The conduits will be placed at a depth of 80 cm below ground level. A red warning mesh will be placed 30 cm above the conduits.

## Lighting Points and Switches

Lighting fixtures will need to be standard so that consumables, tubes and bulbs are readily available on the local market.

The contractor must provide the technical data sheets for the electrical equipment, the calculation notes and the electrical diagrams before the start of the work so that they can be approved by the project manager.

Final sub-circuits complete with accessories and fittings as detailed below and, in the drawing, wired in 20mm diameter conduits concealed in the ceiling:

- Lighting point wired in 3x1.5mm2 SC-PVC-CU cables drawn in 20mm Dia PVC HG conduit complete with all necessary accessories excluding switches and fittings.

- Switching points wired in 3x1.5mm2 SC-PVC-CU cables drawn in 20mm Dia PVC HG conduit complete with all necessary accessories excluding switches and fittings.

- 10A 1 gang SP one/two-way black switch plates as Crabtree ellipse EP071/BK or approved equivalent.

- 10A 2 gang SP two-way black switch plates as Crabtree ellipse EP172/BK or approved equivalent.

- 10A 3 gang SP two-way black switch plates as Crabtree ellipse EP173/BK or approved equivalent.

- 32A isolator complete with contactor and timer for switching the external lights.

### Lighting Fittings

Provide rates to supply, install test and commission the following items. Quotation to include suspension chains, screws, ceiling roses, with an IP21 protection rating and accessories as necessary:

- 40W 600mm x 600mm recessed/surface LED Dali dimmable light complete with driver.

- 12W Surface mounted light at the Veranda as Robus Oyater.

- Wall mounted luminaire with die cast aluminium body as Robus Wega.

- 12W recessed downlight in the circulation lobby or passage as Vtac or Robus.

- Lit emergency Exit light as Sapphire.

- Outdoor lighting– Lighting should preferably be waterproof bulkhead lights or 2000 lumen LED bulbs. Their protection rating should be at least IP54.

### Power Points

Final sub-circuits complete with accessories and fittings as detailed below and in the drawing wired in 20mm diameter conduits concealed in the ceiling:

- Outlet for 13A switched socket outlet complete with concealed 20mm dia. HG PVC conduit, box, ring wiring in 3x2.5mm2 PVC-SC-CU cables but excluding the 13A socket outlet plate.

- 13A twin black moulded and flush switched socket as Crabtree ellipse EP306/3 or approved equivalent.

- 13A single black moulded and flush switched socket as Crabtree ellipse EP304 or approved equivalent.

- 13A twin black moulded and flush switched socket as Crabtree ellipse with 2.1 USB charger.

- Television/F.M / satellite co-axial signal cable in concealed 20mm dia. H/G PVC conduit, square PVC box.

- 2-Way Coaxial Cable Splitter installed in a covered and recessed pattress box outside of the apartment.

- 1G TV Socket as Schneider Lisse or approved equivalent.

- Outlet for 32A DP switch complete with concealed 25mm dia. HG PVC conduit, box, radial wiring in 2C, 4mm2 CU PVC/XLPE/SWA/PVC cables for water heater/instant shower but excluding the 32A DP switch. (AC/ Ventilation fan).

- 32A DP black moulded and flush switch outlet plate as Crabtree Ellipse or approved equivalent

- Security points consisting of 20mm dia. Conduit (without wiring) to the control panel but with draw wires.

Electrical outlets preferably positioned 50 cm from the floor with a minimum protection rating of IP43. A 16 A circuit must not have more than 8 outlets (one circuit for every 4 double outlets). Electrical outlets will be positioned higher up to power the air conditioning systems. These will preferably be placed approximately 30 cm from the appliances.

## Power Distribution

Final sub-circuits complete with accessories and fittings as detailed below and in the drawing wired in 20mm diameter conduits concealed in the ceiling:

- 14-way Recessed/ surface mounted SPN consumer’s unit/Distribution board as Schneider or equal and approved complete with 100A Double Pole integral isolator.

- SP MCB units as Schneider Acti9 or approved equivalent:

  - 10A SP MCB

  - 20A SP MCB

  - 32A SP MCB

  - 40A SP MCB

  - Blanking plates

- Carry out concise permanent labelling for all the sub-circuits.

- Sub-mains cables comprising 3C 10mm2 600/1000V double insulated copper cable from meter box to the consumer unit.

- 38mm for sub-mains cables from the consumer units above

- Allow for 125A Auto changeover for the solar and mains.

- Allow for ceiling mounted sweep fans with a sweep radius of 1.2M. The Fan to be as big ass Fans or approved equivalent.

Distribution boards- The building will be equipped with an electrical panel housing all the power supply connections. This panel will be supplied by a properly sized cable from the main power supply. The line will be protected by a 60 A four-pole circuit breaker with residual current device (RCD).

The distribution cables will have a cross-section that allows them to support a 20% power increase. From the distribution cabinets to the destination, the distribution will be carried out either along cable trays or buried in the walls.

## Supply And Installation of Electrical Appliances

The contractor is responsible for supplying and installing all low-voltage electrical installations and the internal low-voltage distribution network inside the building and their connection to the existing network.

All electrical equipment (light strips, portholes, sockets, fans, air conditioners, etc.) will be installed in accordance with regulations. To ensure the safety and protection of the equipment in operation, it is recommended the use of a single grounding connection on the premises. Care must be taken by the contractor when installing grounding systems.

All equipment (lamps, air conditioners, etc.) used will be of the highest quality and submitted to the project manager for approval before installation. This work will be carried out according to best practices. The work will be performed according to an execution plan, which will be submitted to the project manager for approval.

Drivers' section– They are determined according to the installed power with the following values: lighting – 1.5 mm2 section, power outlet, air circulators – 2.5 mm2 section and air conditioners and water heaters – 4 mm².

Equipment– All materials and technical data sheets provided by the Contractor will be approved by the inspector before installation.

Protection of appliances against electrical hazards– The protection of persons against the dangers presented by electric current will be ensured by grounding of electrical masses and by a device of automatic cut-offs sensitive to the current of associated faults.

Residual current circuit breaker– Each circuit will be protected by a high or medium sensitivity residual current circuit breaker.

All components of the electrical panel will be of the same brand and must comply with standards NF EN 60695-2-11, IEC 60670-24, and IEC 62208, IP30 – IK05.

The distribution panels will be housed in an electrical cabinet comprising:

- A general cut-off by switch (40A, disconnect switch with differential).

- General differential circuit breakers of appropriate rating for the protection of lighting and socket circuits (20 A circuit breaker with 30 mA differential for the electrical socket network, 16 A circuit breaker with 30 mA differential for the interior and exterior lighting network, 20 A circuit breaker with 30 mA differential for the supply of an air conditioning system).

- The general distributors.

- Protection of branch circuits.

- The control components.

- The whole thing will be wired with flexible wire.

The earth conductor will always be identified by the dual green-yellow colouring.

All outgoing cables will exit from the bottom of the enclosure. The cabinet will be designed with a capacity increase of approximately 20%.

All cables must be labeled and their outputs identified. A wiring diagram of the cabinet must be provided with the installation.

The cables must be chosen to withstand external influences and will be of appropriate cross-section according to their use (low voltage, telephone, security, etc.).

Fan– Supply and installation of low-energy rotary fans with a power rating between 50 and 70 W. Diameter between 400 and 450 mm, 220V power supply. The units will be mounted on a fixed frame in a square at a height of approximately 2 m and connected to a Plexo-type switch.

## Grounding of Installations

To ensure an equal potential difference across the entire installation, the tenderer will be responsible for creating an interconnection between the different metal structures and for creating grounding of the main power cabinet.

The equipotential bonding will be achieved using a galvanized steel stake with a minimum depth of 2 meters, connected to a metallic conductor. The conductor may be 26 mm² bare copper, 16 mm² insulated copper, or 50 mm² bare galvanized steel. The connection between the conductor and the stake must remain accessible and be protected against corrosion.

The resistance of this ground connection must be less than 100 Ohms minimum.

Similarly, the grounding of all the different buildings will be achieved by placing a 29mm² copper cable at the bottom of a trench of a depth determined by the EDM technicians. The earth resistance value will be compatible with the rating of the main residual current device.

The busbars will be installed near the main distribution board. The busbar must be connected to the building's metallic structure and the main equipotential bonding connections.

All electrical devices (electrical cabinets, lighting fixtures, power outlets, etc.) as well as the earth terminal of other devices will be connected to the main earth bar. All grounding arrangements will be checked beforehand by the inspector before the work continues.

## Air Conditioning

Supply, installation, and connection of split systems in offices according to plans and specifications. The refrigerant used will be a lower carbon footprint and zero ozone depletion, i.e R410A or R744. The units will be wall-mounted approximately 30 cm from the wall-mounted electrical outlets. Condensate will be drained outside the building (install 25 mm PVC pipe down to ground level).

These units must operate on 220V with an inverter. The minimum basic cooling capacity must be 9000 Btu/h. A technical datasheet for the proposed model must be submitted to us for approval.

## Solar photovoltaic (PV) system

Supply and installation of a 55 kWp solar photovoltaic (PV) system integrated with 85 kWh battery energy storage to provide reliable, renewable electricity to a three-storey building (147 m²).

The facility’s electrical demand includes six 9,000 BTU air conditioning units, lighting (indoor and outdoor), office equipment, water pumping, and household appliances, with an estimated total consumption of 70–75 kWh per day.

Given the high solar resource availability (approximately 5.5–6.0 peak sun hours per day), the PV system is expected to generate approximately 250–300 kWh per day, significantly exceeding the building’s energy demand. This surplus ensures system resilience, supports load variability, and allows for future demand growth.

The 85 kWh battery system (≈68 kWh usable capacity) is designed to supply critical loads during night-time and low-generation periods, ensuring continuity of essential services and reducing dependency on backup generators.

The system will incorporate high-efficiency equipment, load management strategies, and hybrid inverter technology to optimize performance, reliability, and energy utilization.

## Fire Safety - Detection and Protection

The position includes all the work necessary for the supply and implementation of fire protection installations.

- Security alarm point wired in 2x1.5mm2 pvc alarm cables drawn in 20mm Ǿ PVC HG conduit complete with all necessary accessories without outlet place.

- 1-zone Addressable Fire/Security alarm panel as Menvier/GSM/EST.

- Fire Alarm Addressable 1 Zone 1Loop control panel complete with integral printer, graphite finish, integral battery & power supply unit 72hr the control panel to have full network capability, spur torrent soft addressing, 50addresses per loop, charger with temperature compensation built in and checks battery capacity.

- Security keypad.

- Panic buttons.

- Vibration sensors.

- magnetic door contacts.

- Infrared Motion detector.

- Strobe and Siren.

- Smoke Detectors (Optical smoke detectors as Protec 3000/OPHT complete with base plate as MAB800 or Approved equivalent).

- Heat detectors.

- Break glass (Resettable Manual call button/Break glass units.

- Sounder

Portable Fire extinguishers: Supply, deliver, install, test and commission the flowing portable fire extinguishers and conforming to BS EN 3 BS 1449. Water / Carbon Dioxide Gas Fire Extinguisher:

- 9 litres water carbon dioxide gas portable fire extinguisher complete with pressure gauge, initial charge and mounting brackets. Carbon Dioxide Gas Fire Extinguisher.

- 9Kg carbon dioxide gas portable fire extinguisher complete with pressure gauge, initial charge and mountings brackets. Dry Chemical Powder Fire Extinguisher.

- 9Kg chemical powder portable fire extinguisher complete with pressure gauge, initial charge and mountings brackets.

Manual Alarm Bell

- 9 (225mm) manual operated alarm bell (Gong).

FIRE BLANKET

- Fire blanket made of cloth woven with pre-asbestos yarn or any other fireproof material and to measure 1800x1210mm. It shall be fitted with special tapes folded to often instantaneous single action to release blanket from storing jacket to BS 1721 Fire Notices.

- Allow for fire signage for the fire exits and fire instructions to the Project Engineer's approval.

# PLUMBING WORK

Plumbing work to be carried out for the installation of sanitary facilities and connection to the main water supply network. The technical recommendations are as follows:

Internal distribution and connection to appliances –The internal distribution and connection to the devices must be made using the following materials:

- In embedded PPR/PER/Pexi pipe.

- Auto-Plast sleeves for embedded tubes, 6% AG copper brazing.

- Fixing resilient clamps for free expansion.

- Quarter-turn ball valve isolation valves for each sanitary block or group of appliances.

Cold water supply –From the outdoor shut-off valves to the sanitary fixtures, the distribution will be carried out using PPR pipes of the appropriate diameter. The sanitary fixtures will be connected after branching. The isolation valves will be made of brass with a diameter matching the pipes. All internal distribution pipes will be made of PPR or PEX tubing of the appropriate diameter. The pipes will be installed on pipe clamps or embedded in the floor and walls with external protection.

Rainwater drainage –It will be drained via 100mm diameter PVC downpipes from the roof, leading to natural drainage outlets. The contractor will ensure proper drainage of this water by leveling the ground in the yard to prevent any water from pooling.

Wastewater-Sewage– Creation of a separate wastewater and sewage drainage network from sanitary facilities to inspection chambers then directly to the Cesspool. The technical recommendations are as follows:

- The main pipe, which will collect the various wastewater from the sinks, showers, and toilets, will have a diameter of between 110 and 125 mm, be made of PVC, and have a minimum thickness of 3 mm. It will be located outside the building to ensure accessibility.

- The main pipe, which will collect the various wastewater from the toilets and sanitary facilities, will have a diameter between 125 and 160 mm, be made of PVC with a minimum thickness of 3 mm. It will be placed outside the building to ensure accessibility.

- The joint must be secured with glued and chamfered joints. The connections between the different elements must be perfectly watertight.

- Underground pipes must have sufficient slope to allow for easy drainage. If the drain is relatively short (less than 2 m), the slope can be limited to 1 or 2 cm/m. However, beyond 2 m, the slope can reach 2 to 3 cm/m.

- Part of the piping will be placed under the building slab. Check for proper drainage before pouring the concrete.

- The pipes will rest on a layer of sand 100 mm thick.

- The pipes will be connected to inspection chambers, and the connections must be perfectly watertight.

- The tenderer will be responsible for supplying and installing a set of floor drains into the wastewater drainage system. These will be in the centre of the restrooms. The technical recommendations are as follows:

- The model will be plastic with a horizontal outlet, suitable for tiled floors.

- Connection to the drainage network via a PVC pipe with a minimum outside diameter of 40 mm.

- Integrated odor control system.

Drop and collectors–All downpipes and collectors will be made of rigid PVC pipe of the appropriate diameter. They will be installed on removable clamps. The collectors must have a minimum slope of 2% to ensure self-cleaning. Interior downpipes will be protected by either tiling or cement plaster, at the tenderer's expense.

Construction of Cesspool and inspection chambers– The work includes site layout, excavation, foundation slabs, masonry including the sump and inspection chambers, as well as the connection to the toilets.

## Supply And Installation of Sanitary Fixtures

The sanitary fixtures will be made of high-quality white ceramic. The contractor must submit a sample for approval by the project manager.

Restroom “WC”–Supply, installation, and connection to the cold-water supply and the wastewater drainage system for Turkish or English-style toilets (as described in the quote). The technical recommendations are as follows:

- Turkish-style ceramic floor-mounted seat of standard size, approximately 530x600 mm, with non-slip feet.

- Horizontal outlet with a minimum diameter of 100 mm. Connection to the wastewater network via a standard 90° WC pipe with a diameter of 100 mm.

- 6 Litre volume toilet flush with mechanism and straight pipe downpipe with a diameter of 32 mm.

- A 3/8" shut-off valve.

- Connection of the inlet in 3/8" (12/17 mm).

- Set in white.

Wash Hand Basin (WHB)– The price includes the supply, installation, and connection to the cold-water supply and the wastewater drainage system of a set of hand basin-type washbasins. Wash hand basin size 510x 420mm with one tap holes and chain stay hole, 32mm diameter chrome plated chain waste chrome plated non conclusive time delay press action pillar tap as cobra model concealed wall brackets and heavy-duty plastic bottle trap (32mm ‘P’ Trap) with 75mm seal. The wash hand basin to be used as standard or equal and approved.

Shower- This price covers the supply and installation of a complete shower unit, including a chrome-plated exposed shower column, one (or two taps if hot water is supplied) shower faucet with accessories (elbow, chrome handle, etc.), shower head, and column mounting with adjustable brackets. The tenderer will be responsible for the design, installation, and connection of walk-in shower trays to the cold-water supply and wastewater drainage system. The technical recommendations are as follows:

- The shower tray will be made directly on the ground with a concrete border 100 to 200 mm high, 120 to 150 mm wide and covered with non-slip tiles.

- Tray dimensions (width x depth): 1000 x 800 mm

- Installation of an accessible removable PVC siphon and a PVC outlet with an outside diameter of 40 mm for connection to the drainage network.

- Supply of a chrome tap set consisting of a mixer tap with fixed shower head.

- Connection of the inlet in 1/2" (15/21 mm) with installation of a stop valve.

# SPECIFIC PROVISIONS

## Installation of the Water Meter

The work involves bringing the water supply from the main water supply network to the new buildings. This includes excavation to a depth of 1 meter, installation of standard piping, including installation accessories, blue warning tape, and backfilling the trenches. The work also includes the installation of water meter, payment of the subscription fees, and connection of the existing building.

## Installation of an Electricity Meter

The work involves installing a digital meter and connecting it from the electricity grid to the new buildings. Payment of subscription fees and building connection will also be included.

The work includes carrying out excavations (if applicable) up to 1m deep, laying cable trays including installation accessories, warning tape, and closing the trenches.

No interim payments will be made for the water and electricity connection work. This work will not be partially accepted because we need to test all the functionalities before making any payment.

## Security

The work consists of securing the perimeter of the project area with a solid concrete block wall, the base of which is a stone wall. The total length of the perimeter is approximately 660 m.

The foundations will consist of isolated footings. Reinforced concrete columns, 20cm x 30cm, will be placed every 5m along the wall. These columns will rest on an 80cm x 80cm x 30cm footing. A 15cm x 40cm foundation beam will be poured above the stone-wall. Depending on the soil conditions, expansion joints will be incorporated.

The construction work must be carried out according to the above technical specifications; the activities to be carried out are detailed in the quotes and attached plans.

The boundary wall will receive a line of 50cm diameter concertina barbed wire fixed to 50*40mm metal angle brackets. Solid metal gates and metal security barriers will be installed at vehicle access points (entrance and exit of the vicinity).

## Main Building

The work consists of constructing an administrative building that meets the needs of a modern police station.

The building's architecture will be of the 3 multi-storey building, with a total area of ​​approximately 147 m2. The load-bearing structure will be made of reinforced concrete; the brick walls do not have a load-bearing role, serving only to close the empty spaces between the frames.

The Police station building will have:

| Floor | Functionality | No. of rooms |
| --- | --- | --- |
| Ground floor | - Changing rooms - Storage room | - Female changing room + shower - Male changing room + shower - Storage room |
| First Floor | - Social area - Training & meeting room | - Social area - Training & meeting room |
| Second Floor | - Operational zone - Office | - Commander’s office - Operational room |

The structure will be made of reinforced concrete, the footings will be 180x180x45 cm / 150x150x45cm, Columns are 30x30 cm minimum, the beams 20x60 and 20x45 cm.

The slabs will be 150 cm thick with reinforced concrete.

An electrical installation in accordance with energy needs will be carried out, namely: sheathing, wiring, connection to the network, electrical boxes and equipment including earthing work. The wiring and cabling will conform to the execution plans and the paragraphs dedicated to electrical work. The lighting in the offices and bathrooms will be provided by LED lamps of 3000 and 1000 lumens which consume less electricity to reduce the building's energy bill and comply with the environmental protection code.

All rooms and offices at First & Second floors will be ventilated and air-conditioned. The air conditioners will be split R410A type.

A new cesspool of 13.8 m3 usable capacity will be constructed.

## Additional requirements (where applicable)

- Tenderers to submit final quotation, preliminary timeline and implementation plan description as part of the technical offer.

- Contractor to provide detailed timeline, final BOQ and detailed drawings after contract signature. As-built drawings to be provided at the final stage of the project.

- Installation: Included as per this Technical Specifications and annexes.

- This document must be read together with the annexed files.

- CONTINGENCY AND UNSPECIFIED REQUIREMENTS: The Contractor is advised to specify and quote any miscellaneous and accessories necessary to install and make the integrated infrastructure fully operational and efficient.

# APPENDICES

## Technical Data Sheets Requested

| Items for which a form is requested | Minimum required specifications (must be seen on the manufacturer's datasheet) |
| --- | --- |
| Interior lighting |  |
| LED lamp (bulb or strip type) for offices; meeting rooms; bedrooms | Minimum brightness 3000 lumens |
|  | Minimum protection index IP 21 |
| LED lamp (bulb or strip type) for corridors; | Minimum brightness 2000 lumens |
|  | Minimum protection index IP 21 |
| Outdoor lighting and lighting for the toilets |  |
| Window | Minimum brightness 2000 lumens |
|  | Minimum protection index IP 54 |
| LED bulb | Minimum brightness 2000 lumens |
|  | Minimum protection index IP 54 |
| Switches and Sockets |  |
| Single-pole switches | Minimum protection index IP 21 |
| The double ignition switches | Minimum protection index IP 21 |
| Waterproof single-pole switches | Minimum protection index IP 54 |
| Power outlet | Type 2P+T |
|  | Minimum protection index IP 43 |
| Air conditioners |  |
| Air conditioners | Split system with inverter |
|  | R410A or R32 refrigerant |
|  | A minimum protection rating of IP65 |